UNIVERSITY OF MINING AND GEOLOGY “Engineering” LTD Laboratory "Lighting" www.light-bg.eu

Measurement report number 2015-115/17.03.2015

testing samples of products

Model number or type, referring to the manufacturer: LED Luminaire SOFTLINE 48W

Company identification: “Security Smart Systems “Ltd.

Applicant testing:  “Security Smart Systems “Ltd. 6 Gourko str. Vratza

Type of test: control measurements

Measurements have been performed:

- luxmeter PU 550, ID 263621/2586, calibration certificate of the METRA BLANSKO a.s.№2887/2012, 19.12.2012;

- luxmeter KYORITSU 5202, ID K0017929, calibration certificate of the National Centre of Metrology 181-ОИ/15.12.2012;

- luminance-meter L 1003 of angular field 1o, producer “LMT” Germany, ID 0686191, calibration certificate of the National Centre of Metrology 130-ОИ/20.12.2010;

- Ulbricht photometer with diameter 2м;

- Automated goniophotometer.

- Power Meter  HM8115-2 ID 015447345, calibration certificate of the National Centre of Metrology 148-EEИ/14.12.2012;

- Digital thermometer with temperature sensor DS18B20 ID 0000011697CDH, calibration certificate of the National Centre of Metrology 268-TИ/14.11.2012;

- Ampermeter  Д5101 ID 737/1990, calibration certificate of ‘ЛК УНИСИСТ’ Ltd №733/21.11.2012;

- MEGER  UT512 ID 1111074682, calibration certificate of ‘ЛК УНИСИСТ’ Ltd №732/21.11.2012;

- Laser rangefinder DLE-40

- spectroradiometer МК350 ID HS0313220158, test source МК002, calibration certificate of UPRtek lab № А012001 / 2013/7/5

Technical specifications of documentation:  LED Luminaire SOFTLINE 48W

Luminaire

| TEST REPORT 2015-115-17.03.2015 | page 1 | all pages 4 |
| --- | --- | --- |

| TEST REPORT 2015-115-17.03.2015 | page 2 | all pages 4 |
| --- | --- | --- |

Results of test

| Operating voltage | AC 230V | Spectrum of light Kpuls.= 0.4% |
| --- | --- | --- |
| Operating Current | AC 0.245 A |  |
| Wattage including ballast (watts) | 53.0W |  |
| Power factor | 0.96 |  |
| color temperature | 4080 K |  |
| Color rendering index CRI | 80 |  |
| color coordinates CIE 1931 | x=0.3798, y=0.3857 |  |
| color coordinates CIE 1976 | u’=0.2212, v’=0.5054 |  |
| Luminous flux emitted by a luminaire | 4988 lm |  |
| Light output of the luminaire | 94.1 lm /W |  |

Luminaire light distribution of polar coordinates in the conditional flux 1000lm

Luminaire light distribution of the 3D

| TEST REPORT 2015-115-17.03.2015 | page 3 | all pages 4 |
| --- | --- | --- |

Light distribution of luminaries are in tabular form

for conditional luminous flux 1000lm:

gm/C   0   15   30   45   60   75   90  105  120  135  150  165  180

0.0  413  413  413  412  412  412  412  412  412  412  413  413  413

2.5  409  409  408  408  407  407  407  407  407  408  408  409  409

5.0  409  410  409  409  408  406  405  406  408  409  409  410  409

7.5  407  407  406  406  405  404  404  404  405  406  406  407  407

10.0  408  407  406  404  404  403  402  403  404  404  406  407  408

12.5  399  399  397  396  395  395  395  395  395  396  397  399  399

15.0  400  400  399  398  396  396  396  396  396  398  399  400  400

17.5  384  383  382  379  377  377  375  377  377  379  382  383  384

20.0  383  383  382  380  378  377  377  377  378  380  382  383  383

22.5  372  371  370  369  367  366  365  366  367  369  370  371  372

25.0  365  365  364  362  360  359  359  359  360  362  364  365  365

27.5  355  354  354  352  349  348  346  348  349  352  354  354  355

30.0  340  340  339  338  335  335  333  335  335  338  339  340  340

32.5  336  334  333  333  329  327  325  327  329  333  333  334  336

35.0  316  314  312  313  310  309  307  309  310  313  312  314  316

37.5  302  300  298  298  297  297  294  297  297  298  298  300  302

40.0  284  284  281  282  282  283  279  283  282  282  281  284  284

42.5  262  262  261  261  262  263  259  263  262  261  261  262  262

45.0  244  245  246  245  249  249  247  249  249  245  246  245  244

47.5  219  222  223  224  226  229  229  229  226  224  223  222  219

50.0  191  192  207  207  205  210  214  210  205  207  207  192  191

52.5  176  160  182  183  190  185  194  185  190  183  182  160  176

55.0  153  143  149  161  174  162  169  162  174  161  149  143  153

57.5  128  132  131  139  158  143  146  143  158  139  131  132  128

60.0  108  120  122  127  139  128  121  128  139  127  122  120  108

62.5   98  107  104  114  116  112  101  112  116  114  104  107   98

65.0   91   88   89  100   98   98   84   98   98  100   89   88   91

67.5   80   68   77   86   82   81   72   81   82   86   77   68   80

70.0   63   64   70   74   70   67   64   67   70   74   70   64   63

72.5   52   58   58   63   58   59   57   59   58   63   58   58   52

75.0   47   46   43   46   45   47   45   47   45   46   43   46   47

77.5   39   35   37   34   36   38   35   38   36   34   37   35   39

80.0   29   28   29   28   28   29   26   29   28   28   29   28   29

82.5   21   21   20   20   19   19   18   19   19   20   20   21   21

85.0   15   15   14   13   12   13   12   13   12   13   14   15   15

87.5    7    7    7    7    6    6    6    6    6    7    7    7    7

90.0    1    1    1    1    1    1    1    1    1    1    1    1    1

92.5    1    1    1    1    1    1    1    1    1    1    1    1    1

95.0    1    1    1    1    1    1    1    1    1    1    1    1    1

Changing the light flux

| TEST REPORT 2015-115-17.03.2015 | page 4 | all pages 4 |
| --- | --- | --- |

Distribution of illumination in height hanging lamp 5 м

Coordinates of the luminaire X=15m, Y=5m.

Applications:

Files with the EULUMDAT format. Light distribution is captured in γ-С planes with step 2.5о in plane γ (от 0 о - 95 о) и 5о in plane С (от 0 о - 360 о) accordance with EN 13032-1 p 4.2.3.

Files with the measured values

- 2015-115.ldt

(photometric data in a standard format),

Test results relate only to test samples.

Sofia 17.03.2015

The measurements made:

/assoc. prof. d-r. Krasimir Velinov/

Manager:

/ prof. d-r. L. Totev/